September 2012

| Americas Bosch Security Systems, Inc. 130 Perinton Parkway Fairport, New York, 14450, USA Phone: + 1 800 289 0096 Fax: +1 585 223 9180 security.sales@us.bosch.com www.boschsecurity.us | Europe, Middle East, Africa Bosch Security Systems B.V. P.O. Box 80002 5617 BA Eindhoven, The Netherlands Phone: + 31 40 2577 284 Fax: +31 40 2577 330 emea.securitysystems@bosch.com www.boschsecurity.com | Asia-Pacific Robert Bosch (SEA) Pte Ltd, Security Systems 11 Bishan Street 21 Singapore 573943 Phone: +65 6571 2808 Fax: +65 6571 2699 apr.securitysystems@bosch.com www.boschsecurity.asia |
| --- | --- | --- |

Product Guide Specification

SECTION 28 23 29

VIDEO SURVEILLANCE REMOTE DEVICES AND SENSORS

BOSCH NDC-255-P IP DOME CAMERA

- – GENERAL

  - SUMMARY

    - Section Includes

      - Video Surveillance Remote Devices.

    - Related Sections

      - Section [28 23 13 – Video Surveillance Control and Management Systems].

      - Section [28 23 16 – Video Surveillance Monitoring and Supervisory Interfaces].

      - Section [28 23 19 – Digital Video Recorders and Analog Recording Devices].

      - Section [28 23 23 – Video Surveillance Systems Infrastructure].

**********Specifier’s note: Include those standards referenced elsewhere in this SECTION.

  - REFERENCES

    - Australia and New Zealand Standards (AS/NZS)

      - AS/NZS CISPR 22 Information technology equipment - Radio disturbance characteristics - Limits and methods of measurement.

    - Canadian Standards Association (CSA)

      - CAN/CSA-C22.2 N0. 60950-1-03

    - Electromagnetic Compatibility

      - EMC directive 2004/108/EC

    - European Norm

      - EN 50121-4:2006 - Railway applications. Electromagnetic compatibility. Emission and immunity of the signaling and telecommunications apparatus.

      - EN 50130-4:1995 + A1:1998 + A2:2003 - Alarm Systems - Electromagnetic Compatibility - Product Family Standard: Immunity Requirements For Components Of Fire, Intruder And Social Alarm Systems.

      - EN 55022 class B (CE) – Information Technology Equipment – Radio Disturbance Characteristics – Limits and Methods of Measurement for Emission.

      - EN 55024 - Information technology equipment. Immunity characteristics. Limits and methods of measurement

      - EN 60950-1: 2006 (CE), Reference Information Technology Equipment IEC 60950-1: 2005

      - EN 61000-3-2:2006 (CE) Electromagnetic Compatibility – Limits for Harmonic Current Emissions.

      - EN 61000-3-3:1995 + A1:2001 + A2:2005 (CE) Electromagnetic Compatibility – Limits – Limitation of Voltage Changes, Voltage Fluctuations and Limitation of Voltage.

    - Federal Communications Commission (FCC) (www.fcc.gov)

      - FCC CFR 47 part 15 SUBPART B (Class B) – Information Technology Equipment – Radio Disturbance Characteristics – Limits and Methods of Measurement for Emission.

      - ICES-003 Class B - Spectrum Management - Interference-Causing Equipment Standard – Digital Apparatus

    - Institute of Electrical and Electronics Engineers, Inc. (IEEE) (www.ieee.org)

      - IEEE 802.3af Power Over Ethernet.

    - International Organization for Standardization (ISO)

      - 9001 – Quality System.

    - Underwriters Laboratories, Inc. (UL) (www.ul.com)

      - UL 60950-1: 1st edition dated October 31, 2007

  - DEFINITIONS

    - IP Camera: conventional analog camera with an embedded encoder that directly generates IP Video stream.

    - Encoders and Decoders:  devices that transmit video, audio and camera control data to IP Cameras via IP Network such as Ethernet LAN, WAN or Internet.

    - IP Video Management System: video surveillance system that enables users to view video via both a PC and analog monitors.  Comprises a PC Based Host, Video Management Software, IP Cameras, IP Network switch and storage units.

    - iSCSI: refers to protocol, a standardized way to talk to IP-based storage across an IP network.

  - SYSTEM DESCRIPTION

    - Video Surveillance Remote Devices

      - NDC-255-P IP Dome Camera

    - Performance Requirements

      - Complete network video surveillance system inside a compact camera.

      - Progressive scan for sharp images of moving objects.

      - Tri-streaming: Simultaneous dual H.264 streams and one M-JPEG stream.

      - ONVIF compliant.

      - Power over Ethernet (IEEE 802.3af compliant)

      - MicroSD/SDHC card slot for edge recording up to 32 GB.

      - PC surveillance software supports multiple camera monitoring.

      - Two-way audio and audio alarm.

      - Wide range of alarm configuration options for camera tampering and motion detection.

  - SUBMITTALS

    - Submit under provisions of Section [01 33 00].

    - Product Data:

      - Manufacturer’s data, user and installation manuals for all equipment and software programs including computer equipment and other equipment required for complete video management system.

    - Shop Drawings; include

      - System device locations on architectural floor plans.

      - Full Schematic of system, including wiring information for all devices.

    - Closeout Submittals

      - User manual.

      - Parts list.

      - System device locations on architectural floor plans.

      - Wiring and connection diagram.

      - Maintenance requirements.

  - QUALITY ASSURANCE

    - Manufacturer:

      - Minimum of [10] years experience in manufacture and design Video Surveillance Devices.

      - Manufacturer’s quality system: Registered to ISO 9001 Quality Standard.

    - Video Surveillance System

      - Listed by [UL] [EN] [FCC] specifically for the required loads.  Provide evidence of compliance upon request.

    - Installer:

      - Minimum of [5] years experience installing Video IP Surveillance System.

  - DELIVERY, STORAGE AND HANDLING

    - Comply with requirements of Section [01 60 00].

    - Deliver materials in manufacture’s original, unopened, undamaged containers; and unharmed original identification labels.

    - Protect store materials from environmental and temperature conditions following manufacturer’s instructions.

    - Handle and operate products and systems according to manufacturer’s instructions.

    - Bosch provides off-the-shelf availability for our top selling products and same-day or 24-hour shipping.

  - WARRANTY

    - Provide manufacturer’s warranty covering [3] years for replacement and repair of defective equipment.

  - MAINTENANCE

    - Make ordering of new equipment for expansions, replacements, and spare parts available to dealers and end users.

    - Provide factory direct technical support from 8:00 a.m. to 8:00 p.m. via phone and e-mail.

- – PRODUCTS

  - MANUFACTURERS

    - Acceptable Manufacturer:

[Bosch Security Systems, Inc.

130 Perinton Parkway

Fairport, New York, 1450, USA

Phone: + 1 800 289 0096

Fax: + 1 585 223 9180

security.sales@us.bosch.com

www.boschsecurity.us]

[Bosch Security Systems B.V.

P.O. Box 80002

5617 BA Eindhoven, The Netherlands

Phone: + 31 40 2577 284

Fax: +31 40 2577 330

emea.securitysystems@bosch.com

www.boschsecurity.com]

[Robert Bosch (SEA) Pte Ltd, Security Systems

11 Bishan Street 21

Singapore 573943

Phone: +65 6571 2808

Fax: +65 6571 2699

apr.securitysystems@bosch.com

www.boschsecurity.asia]

    - Substitutions: [Not permitted.] [Under provisions of Division 1.]

      - [All proposed substitutions must be approved by the Architect or Engineer professional.]

      - [Proposed substitutions must provide a line-by-line compliance documentation.]

**********Specifier’s note: Select Camera System Series based on project requirement.

  - BOSCH NDC-255-P IP DOME CAMERA

    - General Characteristics:

      - Complete network video surveillance system inside a compact camera.

      - Progressive scan for sharp images of moving objects.

      - Tri-streaming: Simultaneous dual H.264 streams and one M-JPEG stream.

      - ONVIF compliant.

      - Power over Ethernet (IEEE 802.3af compliant)

      - MicroSD/SDHC card slot for edge recording up to 32 GB.

      - PC surveillance software supports multiple camera monitoring.

      - Two-way audio and audio alarm.

      - Wide range of alarm configuration options for camera tampering and motion detection.

    - Camera Functions

      - The camera shall be a stand-alone video surveillance system.

      - The camera shall include a Varifocal 2.8 to 10 mm lens.

      - The camera shall have the ability to encode three video streams simultaneously according to individual customized settings.

      - The camera shall use H.264 compression technology.

      - The camera shall accept power via a Power over Ethernet (IEEE 802.3af) compliant network cable connection.

      - The camera shall allow connection to an optional iSCSI server.

      - The camera kit shall include surveillance software to be installed on a PC.

      - The camera shall contain the following audio capabilities:

        - A microphone to collect and audio signal and the ability to transmit an audio signal to a control station.

        - Allow an operator to communicate messages with the use of an optional loudspeaker.

      - The camera shall contain alarms that signal tampering or movement.

      - The camera shall allow alarm configuration to detect tampering and motion.

      - The camera shall conform to the Open Network Video Interface Forum (ONVIF) standard.

    - Certifications

      - Product

        - CE

        - FCC

        - UL

        - cUL

        - C-tick

        - CB

        - VCCI

      - Power Supply

        - CE

        - UL

        - cUL

        - PSE

        - CCC

    - Power

      - Input Voltage:

        - [+12 VDC]

        - [Power-over-Ethernet]

      - Power consumption: 4.1 W (maximum)

    - Video

      - Sensor Type: 1/4-inch CMOS

      - Sensor Pixels: 640 x 480

      - Sensitivity: 1.0 lux at F1.2

      - Video Resolution:

        - VGA

        - QVGA

      - Video Compression:

        - H.264 MP (Main Profile)

        - H.264 BP+ (Baseline Profile Plus)

        - M-JPEG

      - Frame Rate: 30/25 fps, all resolutions

    - Lens

      - Lens Type: Varifocal 2.8 to 10 mm, DC Iris F1.2 to close

      - Lens Mount: Board mounted

    - Connection

      - Analog Video Out: 2.5 mm jack for installation only

      - Alarm Input: Short or 5 VDC activation

      - Relay Out: Input rating maximum 1 A at 24 VAC/VDC

    - Audio

      - Input:

        - [Built-in microphone]

        - [Line-in jack connector]

      - Output: Line-out jack connector

      - Communication: Two-way, full duplex

      - Compression: G.711

    - Local Storage:

      - Memory Card Slot: Supports up to 32 GB microSD/SDHC card

      - Recording: Continuous recording, ring recording

    - Software Control

      - Unit Configuration: Via Web browser or PC surveillance software

    - Network:

      - Protocols: HTTP, HTTPS, SSL, TCP, UDP, ICMP, RTSP, RTP, RTCP, IGMPv2/v3, SMTP, POP3, FTP, DHCP client, ARP, DNS, DDNS, NTP, SNMP, UPnP

      - Ethernet

        - 10/100 Base-T

        - Auto-sensing

        - Half/full duplex

        - RJ45

      - POE: IEEE 802.3af compliant

    - Mechanical

      - Dimensions:

        - Diameter: 135 mm (5.32 in.)

        - Height: 102 mm (4 in.)

      - Weight: 548 g (1.21 lb)

    - Environmental

      - Operating Temperature

        - Camera: -10°C to +50°C (+14°F to +122°F)

        - Universal Power Supply Unit: 0°C to +40°C (+32°F to +104°F)

      - Storage Temperature: -20°C to +70°C (-4°F to +158°F)

      - Humidity: 10% to 80% relative humidity (non-condensing)

- – EXECUTION

  - EXAMINATION

    - Examine areas to receive devices and notify adverse conditions affecting installation or subsequent operation.

    - Do not begin installation until unacceptable conditions are corrected.

  - PREPARATION

    - Protect devices from damage during construction.

  - INSTALLATION

    - Install devices in accordance with manufacturer’s instruction at locations indicated on the floor drawings plans.

    - Ensure selected location is secure and offers protection from accidental damage.

    - Location must provide reasonable temperature and humidity conditions, free from sources of electrical and electromagnetic interference.

  - FIELD QUALITY CONTROL

    - Test snugness of mounting screws of all installed equipment.

    - Test proper operation of all video system devices.

    - Determine and report all problems to the manufacturer’s customer service department.

  - ADJUSTING

    - Make proper adjustment to video system devices for correct operation in accordance with manufacturer’s instructions.

    - Make any adjustment of camera settings to comply with specific customer’s need.

  - DEMONSTRATION

    - Demonstrate at final inspection that video management system and devices function properly.

END OF SECTION

# Text boxes

Specifier Notes:  This product guide specification is written according to the Construction Specifications Institute (CSI) 3-Part Format, based on MasterFormat 2004 and The Project Resource Manual—CSI Manual of Practice. The Manufacturer is responsible for technical accuracy.

The section must be carefully reviewed and edited by the Architect or Engineer to meet the requirements of the project and local building code.  Words and sentences within brackets [ ] are choices to include or exclude a particular item or statement.  Coordinate this section with other specification sections and the Drawings.  Delete all “Specifier Notes” after editing this section.